## Sheet1
Component | Node No. | frequency |  | Type | Fragility curve (PGA based) |  |  |  | Fragility curve (response based)
|  | Low | High |  | Failure mode | βr | βu | βc | Am (Idaho) | Am (Los Alamos) | β
1. DC Motor Control Center (MCC) | 1712 | 3 | 10 | avg | Loss of function | 0.3 | 0.35 | 0.46098 | 13.0826 | 22.8066 | 0.46098
2. Battery | 699 | 10 | 15 | avg | Loss of function | 0.3 | 0.35 | 0.46098 | 3.6074 | 6.0601 | 0.46098
3. Reactor coolant pump | 278 | 7 | 10 | avg | Support failure | 0.3 | 0.4 | 0.5 | 2.8345 | 4.7315 | 0.5
4. Air handler | 744 | 10 | 20 | avg | Loss of function | 0.3 | 0.4 | 0.5 | 3.0943 | 5.1738 | 0.5
5. HVAC duct | 1085 | 2 | 20 | peak | Support failure | 0.35 | 0.5 | 0.61033 | 30.4155 | 50.3946 | 0.61033
6. Containment | 1898, 259 | 5 | 10 | avg | Structural failure | 0.3 | 0.35 | 0.46098 | 2.9539 | 5.0063 | 0.46098
7. Reactor pressure vessel | 259 | 10 | 33 | avg | Support failure | 0.3 | 0.35 | 0.46098 | 1.7342 | 2.9791 | 0.46098
8. Piping | 1665, 1649, 778 | 4 | 33 | Max | Boundary failure | 0.3 | 0.5 | 0.5831 | 28.7899 | 47.5524 | 0.5831
*Factor: to convert median of fragility curve to spectral acceleration
Note on K2: Yu, Ching Ching: Am=HCLPF*e^(1.65(βr+βu))